|  |  |  |  | SITE ACTIVITY REPORT |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Customer Name |  |  |  |  |  | FE Name |  |  |  |  |  |
| Site Name |  |  |  |  |  | W.O. Nr. |  |  |  |  |  |
| Contact Name |  |  |  |  |  | W.O. Start / Finish |  | 9/11/2020 to 9/11/2020 |  |  |  |
| PO / Contract Nr. |  |  |  |  |  | Report Date |  | 9/12/2020 |  |  |  |
| Package Information |  |  |  |  |  |  |  |  |  |  |  |
| PD Number | Customer Tag |  | Package SN |  | Package Hours |  | Package Starts |  | Engine SN | Engine Hours | Engine Starts |
| 3895x | No Tag |  | CG837xx |  | 281754 |  | 1967 |  | OHB16- C37xx | 20854 | 252 |

TABLE OF CONTENTS

SECTION 1 – PURPOSE OF VISIT	2

SECTION 2 – SUMMARY OF VISIT	2

SECTION 3 – RECOMMENDATIONS	2

SECTION 4 – ACTION ITEMS	2

SECTION 5 – TASK SUMMARY	3

SECTION 6 – DAILY SITE SUMMARY	3

SECTION 7 – TIMESHEET	12

# SECTION 1 – PURPOSE OF VISIT

To perform a borescope inspection/condition assessment on the C40 Genset at Ingredion.

# SECTION 2 – SUMMARY OF VISIT

Borescope inspection was completed – see report for more details. Overall, the package is in acceptable condition. Unit has been preserved following Solar’s standard preservation practices.

# SECTION 3 – RECOMMENDATIONS

Continue to communicate with Solar for any additional needs.

# SECTION 4 – ACTION ITEMS

| Created Date | Due Date | Package S/N | Description | Responsible Party | Status |
| --- | --- | --- | --- | --- | --- |

# SECTION 5 – TASK SUMMARY

Customer Tag:	No Tag

Package S/N:	CG837xx

| Task Name | Finish Date | Status |
| --- | --- | --- |
| Borescope Inspection - C40 C50 T60 | 9/11/2020 | Completed |

# SECTION 6 – DAILY SITE SUMMARY

Friday, September 11, 2020

Daily Site Summary

Completed JSA, TRAAC and reviewed WHA Walked down LOTO - Gas fuel supply and pneumatic start motor supply were already locked out - All breakers in MCC room were turned off - CO2 fire suppression solenoid was already removed from CO2 bottle Unloaded tools from truck Prepped unit for Engine and RGB borescope inspection Completed Engine and RGB borescope inspection - See report for more details Reassembled fuel injectors, T5 thermocouples and borescope ports Took pictures of package components shown below - Overall the package is dirty but all devices appear to be in acceptable condition - May be necessary to replace gaskets/bolts on gas fuel supply - Air inlet pre-filters should be replaced - CO2 bottles should be inspected – last time they were inspected was April 2012 - Marman clamp on exhaust diffuser is not installed correctly leaving gap between exhaust and package wall - Coupling cover was removed – no damage found on coupling - Control cabinet electrical devices appear to be working and in good condition