## Sheet1
Model | Taurus60 | Taurus70 | Titan130
ISO Rated Power (MW) | 5.67 | 7.965/8.18 | 16.529
Rated Voltage (kV) | 10.5 | 10.5 | 10.5
Power Generation Heat Rate (kJ/kWh) | 11427 | 10504/10467 | 10159
Power Generation Efficiency (%) | 31.5 | 34.27/34.39 | 35.43
Fuel Consumption (m³/h) | 1852 @35MJ/m³（LHV） | 2390/2446 | 4797
Exhaust Gas Temperature (℃) | 510 | 511/520 | 489
Exhaust Gas Flow Rate (kg/h) | 78385 | 96700/96596 | 202512
Dimensions (m) | 11.73*3.91*9.25 | 13.38*4.36*9.59 | 17.52*4.84*9.43
Total Weight (t) | ≈75 | ≈89 | ≈105
Auxiliary Power Consumption (kW) | 37.5 | 38 | 87
Starting Motor Power (kW) | 92 | 112 | 2*112
Compressed Air Consumption (Nm³/min) | ＜1 @689-1378kpa | ＜1 | ＜1
Lube Oil Capacity (L) | ≈1600 | ≈3000 | ≈4200
Cooling Method | Generator: Air-cooled; Lube Oil: Air-cooled / Water-cooled | Generator: Air-cooled; Lube Oil: Air-cooled / Water-cooled | no generator
NOx Emission (mg/Nm³) | ≤30 (Above 50% load, @15% O2) | ≤30 | ≤30
Noise Level dB(A) | ≤85 @1m distance, 1.5m height | ≤85 | ≤85
Saturated Steam Production (t/h) | 12.9 (ISO condition, 1.0 MPaG) | 16.6/17.1 | 30.9