## Sheet1
SERVICE ORDER DATE OPEN | PLANT No. | SMR | ASSIGNMENT TYPE | ERROR CAUSE | ACTION TAKEN | M3 SO Number | Remark | STATUS | PLANT Nos. | ASSIGNMENT TYPE | ERROR SYMPTOM | ERROR CAUSE | ACTION TAKEN | OIL SAMPLE RESULT | G # | PlantNumbers
2017-10-28 | XDRN003 (G#3) | 4226 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0019 - Replaced Filters | S0 1 | Carried out E40 Service @4000hrs, Oil result no. 790629 dated 6 nov 2017. | OPEN- WIP |  | Reactive Visit - Non Failure | 50Y- Annual Inspection Due | C0002 - Actuator | A0001 - Adjusted Settings | N/A | genset | XDRN001 (G#1) | 1
31/10/2017 | XDRN001 (G#1) | 5365 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | S0 2 | Replaced Air Filters | CLOSED- AWAITING TECHNICAL FEEDBACK |  | Reactive Visit, Breakdowns, Problems | S0010 - Breaker Tripping | C0007 - Air Flap | A0002 - Clean/Wash | NORMAL | genset | XDRN002 (G#2) | 3
31/10/2017 | XDRN004 (G#4) | 5258 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | S0 3 | Replaced Air Filters | CLOSED |  | Proactive Visit | 50H - Change Separator Element | C0008 - Air Flow Blocked | A0003 - Cleaned Coils | BORDERLINE | genset | XDRN003 (G#3) | 4
2017-11-01 | XDRN002 (G#2) | 4917 | Reactive Visit, Breakdowns, Problems | C0079 - Oil - Low/High | A0018 - Replaced / Installed Component | S0 4 | Replaced Pressure transmiter Oil |  |  | E40 - MWM Periodic Maintenance (medium) | S0012 - Commission Set Up as Per Aggreko Spec | C0009 - Alternator: Battery | A0004 - Commissioned Equipment | URGENT | genset | XDRN004 (G#4) | 5
2017-11-01 | XDRN003 (G#3) | 4439 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | S0 5 | Replaced Air Filters |  |  | E50 - MWM Periodic Maintenance (Extended) | S0014 - Customer Requested Equipment Adjustment | C0010 - Ambient Temperature - High or Low | A0006 - De-Commissioned Equipment | CRITICAL | genset | SO ITEM | 6
2017-11-16 | XDRN002 (G#2) | 4922 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 6 | Replaced Spark Plug ( Cylinder A2,A4,A5,A6,A8,B1,B5,B7,B8 ) |  |  | E60 - MWM Intermediate Overhoule | S0015 - Decommission / Job Take Down | C0011 - AVR - Automatic Voltage Regulator | A0008 - Drained Skid / Bund Fluids |  | genset |  | 7
2017-11-17 | XDRN003 (G#3) | 4552 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 7 | Replaced Spark Plug( Cylinder A1 ) |  |  | E20 - MWM Daily Inspection Round | S0016 - Disassemble Unit | C0012 - Battery - Drained / Fault / Terminals | A0010 - Load / Performance Test |  | genset |  | 8
2017-11-18 | XDRN003 (G#3) | 4558 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 8 | Replaced Spark Plug( Cylinder A7 ) |  |  | 11 - Audit Action | S0017 - Equipment Cleaning Due | C0013 - Battery - Isolator | A0012 - Painted |  | genset |  | 9
2017-11-18 | XDRN002 (G#2) | 4929 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 9 | Replaced Spark Plug( Cylinder B5 ) |  |  | 33- Retrofit / Service Buletin | S0018 - Equipment Cycles On and Off | C0014 - Bearing - Failure | A0013 - Preventative Maintenance |  | genset |  | 10
2017-12-11 | XDRN004 (G#4) | 5691 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 10 | Replaced Spark Plug( Cylinder B3 & B4 ) |  |  |  | S0019 - Equipment Not Performing | C0015 - Belts - Loose or Broken | A0014 - Primed Fuel System |  | genset |  | 11
2017-12-21 | XDRN002 (G#2) | 5112 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | S0 11 | Replaced Air Filters |  |  |  | S0020 - Equipment Physically Damaged | C0016 - Belts - Tensioner / Idler | A0017 - Repaired Component |  | genset |  | 12
2018-01-04 | XDRN002 (G#2) | 5172 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 12 | Replaced Spark Plug( Cylinder B2) |  |  |  | S0021 - Equipment Stopped Running | C0017 - Breaker - Control | A0018 - Replaced / Installed Component |  | genset |  | 13
2018-01-04 | XDRN004 (G#4) | 5918 | Proactive Visit | C0007 - Air Flap | A0003 - Cleaned Coils | S0 13 | Cleaning Flame trap cyilinder B3 and B4 |  |  |  | S0022 - Equipment Warning Light On | C0019 - Breaker - Main | A0019 - Replaced Filters |  | genset |  | 14
2018-01-04 | XDRN003 (G#3) | 5235 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 14 | cleaning intake manifold |  |  |  | S0023 - Equipment Will Not Start / Stop | C0020 - Capacitor Failure | A0020 - Replenished Fluids (Coolant/Freon/Oil) |  | genset |  | 15
2018-01-05 | XDRN001 (G#1) | 6039 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 15 | cleaning intake manifold |  |  |  | S0026 - Fleet Verification Required | C0024 - Controller - (HMI, PLC, I/O board, etc.) | A0021 - Reset Component |  | genset |  | 16
2018-01-05 | XDRN002 (G#2) | 5175 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 16 | cleaning intake manifold |  |  |  | S0027 - Flow Rate Incorrect (High/Low) | C0025 - Coolant Mixture / Level | A0022 - Restarted Unit |  | genset |  | 17
2018-01-06 | XDRN002 (G#2) | 5186 | Reactive Visit, Breakdowns, Problems | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 17 | Replaced Spark Plug( Cylinder B4) |  |  |  | S0028 - Frequency Incorrect / Unstable | C0026 - Cooler - After | A0024 - Swapped Unit |  | genset |  | 18
2018-01-07 | XDRN003 (G#3) | 5238 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | S0 18 | Replaced Air Filters |  |  |  | 50G - Fuel Tank Inspect / Test Due | C0027 - Cooler - Fuel or Oil | A0028 - Disassembled Equipment |  | genset |  | 19
2018-01-09 | XDRN003 (G#3) | 5238 | Reactive Visit - Non Failure | C0002 - Actuator | Site Consumption | S0 19 | Cleaning Throtlle Valve ( Accuator ) |  |  |  | S0030 - Leaks: Equipment | C0029 - Coupling / Alignment | A0030 - Fabricated Component |  | genset |  | 20
2018-01-10 | XDRN002 (G#2) | 5203 | Reactive Visit, Breakdowns, Problems | C0075 - Motor Starter | A0018 - Replaced / Installed Component | S0 20 | Pinion Air Stater damage engine not start |  |  |  | 50K - Oil Sample Due | C0030 - CT - Current Transformer / Module | A0031 - Follow-up Not Required |  | genset |  | 21
2018-01-11 | XDRN001 (G#1) | 6119 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | S0 21 | Sample oil |  |  |  | S0036 - Pressure Incorrect (High/Low) | C0031 - Customer / Contract Requirement | A0032 - Follow-up Required |  | genset |  | 22
2018-01-11 | XDRN003 (G#3) | 5278 | Proactive Visit | C0075 - Motor Starter | Site Consumption | S0 22 | Check and Add oil air stater |  |  |  | S0037 - Proactive Visit with no problems | C0037 - Earth Leakage / Ground Fault | A0033 - Oil Sample Taken |  | genset |  | 23
2018-01-12 | XDRN004 (G#4) | 6008 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | S0 23 | Replaced Air Filters |  |  |  | 50K - Oil Sample Due | C0030 - CT - Current Transformer / Module | A0034 - Report Submitted |  | genset |  | 21
2018-01-14 | XDRN003 (G#3) | 5331 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 24 | Greasing Bearing Generator every 700 hour |  |  |  | 50A - SERVICE - A Due | C0039 - Engine Failed | A0032 - Follow-up Required |  | genset |  | 25
2018-01-16 | XDRN004 (G#4) | 6050 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 25 | Cleaning Condensator every 250 hour |  |  |  | 50B - SERVICE - B Due | C0040 - Environment - Dirty | A0036 - Return Component to SRC |  | genset |  | 26
2018-01-16 | XDRN002 (G#2) | 5203 | Reactive Visit, Breakdowns, Problems | C0075 - Motor Starter | A0018 - Replaced / Installed Component | S0 26 | Repair air stater change pinion gear |  |  |  | 50C - SERVICE - C Due (Health Check) | C0041 - E-Prom | A0037 - Unit to be Scrapped |  | genset |  | 27
2018-01-16 | XDRN002 (G#2) | 5203 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 27 | Cleaning Condensator every 250 hour |  |  |  | 50L - Fuel Service - Change Filters | C0042 - ESD - Emergency Shutdown | A0039 - Repaired/Replaced by vendor |  | genset |  | 28
2018-01-17 | XDRN004 (G#4) | 6051 | Reactive Visit - Non Failure | C0002 - Actuator | A0013 - Preventative Maintenance | S0 28 | Cleaning Throtlle Valve ( Accuator ) |  |  |  | S0040 - Smokes Excessively | C0043 - Fan | A0040 - Audit Action Completed |  | genset |  | 29
2018-01-18 | XDRN001 (G#1) | 6216 | Reactive Visit, Breakdowns, Problems | C0002 - Actuator | A0013 - Preventative Maintenance | S0 29 | Cleaning Throtlle Valve and change bearing side A ( Accuator ) |  |  |  | S0043 - Temperature Too High or Too Low | C0044 - Fan - Sequencer | A0041 - Plant/Unit Out of Service |  | genset |  | 30
2018-01-20 | XDRN002 (G#2) | 5258 | Reactive Visit, Breakdowns, Problems | C0103 - Sensor - Temp (RTD, Thermocouple,etc) | A0018 - Replaced / Installed Component | S0 30 | Replaced termocouple A6 |  |  |  | S0044 - Voltage - Incorrect / Unstable / None | C0045 - Filter - Air | A0042 - 3rd Party Repair/Recondition |  | genset |  | 31
2018-01-20 | XDRN003 (G#3) | 5454 | Reactive Visit - Non Failure | C0007 - Air Flap | A0003 - Cleaned Coils | S0 31 | Cleaning Flame trap cyilinder A5,A6,B7 and B8 |  |  |  | S0045 - Burning Smell | C0047 - Filter - Fuel | A0043 - No Action Taken |  | genset |  | 32
2018-01-21 | XDRN003 (G#3) | 5463 | Reactive Visit - Non Failure | C0007 - Air Flap | A0003 - Cleaned Coils | S0 32 | Cleaning Flame trap cyilinder A5 and A6 |  |  |  | S0046 - Fire | C0048 - Filter - Oil | A0044 - Resolved Over Phone |  | genset |  | 33
2018-01-22 | XDRN004 (G#4) | 5467 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 33 | Change spark plug all 16 cylinder use sparkplug 9 hole |  |  |  | S0047 - Investigate Issue: Action Required | C0050 - Filter - Water | Site Consumption |  | genset |  | 34
2018-01-22 | XDRN004 (G#4) | 6135 | Proactive Visit | C0040 - Environment - Dirty | A0019 - Replaced Filters | S0 34 | Change gas filter |  |  |  | S0052 - M06 Required | C0051 - Fluid Leaks |  |  | genset |  | 35
2018-01-25 | XDRN003 (G#3) | 5533 | Reactive Visit, Breakdowns, Problems | C0002 - Actuator | Site Consumption | S0 35 | Cleaning Throtlle Valve and change bearing side A ( Accuator ) |  |  |  | S0053 - M07 Required | C0053 - Fuel - Contaminated |  |  | genset |  | 36
2018-01-27 | XDRN001 (G#1) | 6311 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 36 | Cleaning Condensator every 250 hour |  |  |  | S0054 - Major Component / Fleet Failure | C0054 - Fuse |  |  | genset |  | 37
2018-01-27 | XDRN003 (G#3) | 5549 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 37 | Cleaning Condensator every 250 hour |  |  |  | S0055 - Audit Action Required | C0055 - Gasket / ORing / Seal Failure |  |  | genset |  | 38
2018-01-27 | XDRN004 (G#4) | 6159 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 38 | Cleaning Condensator every 250 hour |  |  |  | S0056 - Technical Bulletin: Action Required | C0057 - Generator End Failure |  |  | genset |  | 39
2018-01-27 | XDRN004 (G#4) | 6159 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 39 | Cleaning Radiator |  |  |  | S0057 - Abnormal Oil Sample | C0058 - Heater - Element/Electrode |  |  | genset |  | 40
2018-01-28 | XDRN003 (G#3) | 5554 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 40 | Cleaning Radiator |  |  |  | S0058 - Technical Analysis-"written description" | C0059 - Hose / Fitting - Air |  |  | genset |  | 41
2018-01-28 | XDRN001 (G#1) | 6318 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 41 | Cleaning Radiator |  |  |  | S0006 - Technician Inventory | C0060 - Hose / Fitting - Fuel |  |  | genset |  | 42
2018-01-30 | XDRN002 (G#2) | 5429 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | S0 42 | Sample oil |  |  |  | Site Consumption | C0061 - Hose / Fitting - Oil/Freon |  |  | genset |  | 43
2018-02-04 | XDRN003 (G#3) | 5641 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | S0 43 | Sample oil |  |  |  |  | C0062 - Hose / Fitting - Water/Coolant |  |  | genset |  | 44
2018-02-12 | XDRN001 (G#1) | 6490 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 44 | Cleaning Air filter generator and greasing bearing generator |  |  |  |  | C0064 - Injectors |  |  | genset |  | 45
2018-02-12 | XDRN002 (G#2) | 5591 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 45 | Cleaning Air filter generator |  |  |  |  | C0137 - Lights |  |  | genset |  | 46
2018-02-12 | XDRN003 (G#3) | 5766 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 46 | Cleaning Air filter generator
2018-02-12 | XDRN004 (G#4) | 6239 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 47 | Cleaning Air filter generator |  |  |  |  | C0065 - Magnetic Pick-Up |  |  | genset |  | 47
2018-02-17 | XDRN001 (G#1) | 6490 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S0 48 | Cleaning flame trap |  |  |  |  | C0065 - Magnetic Pick-Up |  |  | genset |  | 48
2018-02-19 | XDRN002 (G#2) | 5643 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 49 | Check and Add oil air stater |  |  |  |  | C0068 - Module - Engine Control (ECM) |  |  | genset |  | 49
2018-02-19 | XDRN003 (G#3) | 5823 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 50 | Check and Add oil air stater |  |  |  |  | C0069 - Module - Load Share |  |  | genset |  | 50
2018-02-19 | XDRN004 (G#4) | 6241 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 51 | Check and Add oil air stater |  |  |  |  | C0070 - Module - Synchronizer |  |  | genset |  | 51
2018-02-19 | XDRN004 (G#4) | 6241 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S0 48 | Carried out B service (Valve lag check & adjustment) & Cleaning Flame Trap |  |  |  |  | C0071 - MOP - Motorized Potentiometer |  |  | genset |  | 52
2018-02-20 | XDRN001 (G#1) | 6539 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S0 49 | Oil sample Oil result no. 87030 dated 28 Feb 2018. |  |  |  |  | C0072 - Motor Failure - (Fan, Blower, etc.) |  |  | FS
2018-02-21 | XDRN003 (G#3) | 5825 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S0 50 | Carried out E40 Service @4000hrs, Oil result no. 82380 dated 28 Feb 2018. |  |  |  |  | C0073 - Motor Mech
2018-02-21 | XDRN003 (G#3) | 5825 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S0 51 | Cleaning flame trap |  |  |  |  | C0074 - Motor Overloads
2018-02-24 | XDRN002 (G#2) | 5702 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S0 52 | Cleaning flame trap |  |  |  |  | C0075 - Motor Starter
2018-02-27 | XDRN001 (G#1) | 6629 | Reactive Visit, Breakdowns, Problems | C0102 - Sensor - Pressure | A0018 - Replaced / Installed Component | S0 53 | Replaced Transmiter 30 Mbar |  |  |  |  | C0077 - No Problem Found
2018-03-07 | XDRN001 (G#1) | 5766 | Reactive Visit, Breakdowns, Problems | C0075 - Motor Starter | A0013 - Preventative Maintenance | S0 54 | change seal air stater |  |  |  |  | C0078 - Nozzle Blocked
2018-03-08 | XDRN002 (G#2) | 6790 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 55 | check and Add oil air stater |  |  |  |  | C0079 - Oil - Low/High
2018-03-08 | XDRN003 (G#3) | 5966 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 56 | check and Add oil air stater |  |  |  |  | C0083 - Panel Damage
2018-03-12 | XDRN003 (G#3) | 6026 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 57 | Greasing Bearing generator |  |  |  |  | C0084 - Parameter Adjustment
2018-03-13 | XDRN003 (G#3) | 6041 | Proactive Visit | C0045 - Filter - Air | A0013 - Preventative Maintenance | S0 58 | Change Air filter |  |  |  |  | C0085 - Phase Monitor
2018-03-14 | XDRN001 (G#1) | 6858 | Reactive Visit, Breakdowns, Problems | C0002 - Actuator | A0013 - Preventative Maintenance | S0 59 | Cleaning thortlle valve & change bearing thortle |  |  |  |  | C0086 - PMG
2018-03-14 | XDRN001 (G#1) | 6858 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 60 | Replaced Spark Plug( Cylinder A4 ) |  |  |  |  | C0087 - Preventive Maintenance Due
2018-03-15 | XDRN003 (G#3) | 6079 | Reactive Visit, Breakdowns, Problems | C0002 - Actuator | A0013 - Preventative Maintenance | S0 61 | Cleaning thortlle valve & change bearing thortle |  |  |  |  | C0088 - PT - Power Transformer
2018-03-15 | XDRN003 (G#3) | 6079 | Reactive Visit, Breakdowns, Problems | C0103 - Sensor - Temp (RTD, Thermocouple,etc) | A0018 - Replaced / Installed Component | S0 62 | Change thermo element exhaust ATL |  |  |  |  | C0089 - Pump - Fuel
2018-03-15 | XDRN001 (G#1) | 6868 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 63 | Cleaning condestator |  |  |  |  | C0090 - Pump - LTA
2018-03-16 | XDRN004 (G#4) | 6640 | Reactive Visit, Breakdowns, Problems | C0002 - Actuator | A0013 - Preventative Maintenance | S0 64 | Cleaning and Change bearing thortlle valve |  |  |  |  | C0091 - Pump - Oil
2018-03-16 | XDRN004 (G#4) | 6640 | Proactive Visit | C0007 - Air Flap | A0003 - Cleaned Coils | S0 65 | Cleaning flame trap B7 and B8 |  |  |  |  | C0092 - Pump - Water
18/03/2018 | XDRN001 (G#1) | 6909 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 66 | change spark plug A3 |  |  |  |  | C0094Racor Ball Kit
20/03/2018 | XDRN004 (G#4) | 6643 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 67 | Change spark plug B5,B6,B7 |  |  |  |  | C0095 - Radiator
20/03/2018 | XDRN001 (G#1) | 6154 | Proactive Visit | C0077 - No Problem Found | A0033 - Oil Sample Taken | S0 68 | Oil sample Taken |  |  |  |  | C0097 - Relay - Failure
21/03/2018 | XDRN001 (G#1) | 6912 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 69 | Change spark plug A4 and B3 |  |  |  |  | C0099 - Rotating Rectifier / Diodes
21/03/2018 | XDRN003 (G#3) | 6204 | Proactive Visit | C0077 - No Problem Found | Site Consumption | S0 70 | Cleaning condestator |  |  |  |  | C0100 - Scale Build Up
22/03/2018 | XDRN001 (G#1) | 6924 | E40 - MWM Periodic Maintenance (medium) | C0007 - Air Flap | A0003 - Cleaned Coils | S0 71 | Carried out B service (Valve lag check & adjustment) |  |  |  |  | C0101 - Sensor - Level
24/03/2018 | XDRN003 (G#3) | 6253 | E40 - MWM Periodic Maintenance (medium) | C0007 - Air Flap | A0003 - Cleaned Coils | S0 72 | Carried out B service (Valve lag check & adjustment) |  |  |  |  | C0102 - Sensor - Pressure
2018-03-24 | XDRN002 (G#2) | 5898 | Proactive Visit | C0077 - No Problem Found | A0033 - Oil Sample Taken | S0 73 | Oil sample Taken |  |  |  |  | C0107 - Skid / Bund Fluid Level High
2018-03-25 | XDRN002 (G#2) | 5918 | E40 - MWM Periodic Maintenance (medium) | C0007 - Air Flap | A0039 - Repaired/Replaced by vendor | S0 74 | Carried out B service (Valve lag check & adjustment) |  |  |  |  | C0108 - Solenoid - Slave
2018-03-25 | XDRN004 (G#4) | 6739 | Proactive Visit | Site Consumption | A0013 - Preventative Maintenance | S0 75 | Cleaning condestator |  |  |  |  | C0109 - Starter - Engine
2018-04-06 | XDRN004 (G#4) | 6937 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | S0 76 | Oil sample Taken |  |  |  |  | C0110 - Strainer - Clogged
2018-04-08 | XDRN003 (G#3) | 6461 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 77 | Cleaning condestator |  |  |  |  | C0111 - Structural Failure
2018-04-08 | XDRN003 (G#3) | 6461 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 78 | Add oil stater |  |  |  |  | C0112 - Switch - Flow
2018-04-08 | XDRN001 (G#1) | 7111 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 79 | Cleaning condestator |  |  |  |  | C0113 - Switch - Level
2018-04-09 | XDRN001 (G#1) | 7136 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | S0 80 | Oil sample Taken |  |  |  |  | C0114 - Switch - Position
2018-04-09 | XDRN004 (G#4) | 7003 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 81 | Cleaning Condestator |  |  |  |  | C0115 - Switch - Pressure
2018-04-09 | XDRN004 (G#4) | 7003 | Proactive Visit | C0045 - Filter - Air | A0013 - Preventative Maintenance | S0 82 | Change Air filter |  |  |  |  | C0116 - Switch - Speed
2018-04-10 | XDRN001 (G#1) | 7159 | Proactive Visit | C0045 - Filter - Air | A0013 - Preventative Maintenance | S0 83 | Change Air filter |  |  |  |  | C0117 - Thermostat
2018-04-13 | XDRN001 (G#1) | 7189 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 84 | Greasing Bearing generator |  |  |  |  | C0118 - Timer
2018-04-15 | XDRN004 (G#4) | 7051 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | S0 89 | Change spark plug A4,A5, B1,B2,B7 |  |  |  |  | C0119 - Transducer
2018-04-17 | XDRN003 (G#3) | 6614 | Reactive Visit, Breakdowns, Problems | C0101 - Sensor - Level | A0018 - Replaced / Installed Component | S0 90 | Replaced Oil solenoid shutoff Valve ( out Stock ) |  |  |  |  | C0121 - Turbo
2018-04-18 | PLTMG RENGAT SOITEM | N/A | Proactive Visit | C0080 - Other "Written Description" | A0011 - Other "Written Description" | S0 91 | Site Compsumption Montly 1- Top Up on New oil Tank |  |  |  |  | C0122 - Valve - 3-Way
2018-04-27 | XDRN004 (G#4) | 7236 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0019 - Replaced Filters | S0 92 | Carried out E40 Service @4000hrs, Oil sample result no.790629 dated 6 nov 2017. |  |  |  |  | C0127 - Valve - Check Valve
30/04/2018 | XDRN003 (G#3) | 7342 | Proactive Visit | C0002 - Actuator | A0013 - Preventative Maintenance | S0 93 | Cleaning thortlle valve |  |  |  |  | C0131 - Valve - Manual
2018-05-01 | XDRN001 (G#1) | 7289 | Proactive Visit | C0002 - Actuator | A0013 - Preventative Maintenance | S0 94 | Cleaning thortlle valve |  |  |  |  | C0132 - Valve - Pressure Relief Valve
2018-05-01 | XDRN003 (G#3) | 6870 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 95 | Add oil stater |  |  |  |  | C0134 - Valve - Solenoid
2018-05-02 | XDRN004 (G#4) | 6878 | Proactive Visit | C0002 - Actuator | A0013 - Preventative Maintenance | S0 96 | Cleaning thortlle valve |  |  |  |  | C0136 - Wiring / Connection Fault
2018-05-04 | XDRN004 (G#4) | 6909 | Proactive Visit | C0095 - Radiator | A0013 - Preventative Maintenance | S0 97 | Cleaning radiator |  |  |  |  | C0142 - Camshaft
2018-05-04 | XDRN002 (G#2) | 5956 | Proactive Visit | C0095 - Radiator | A0013 - Preventative Maintenance | S0 98 | Cleaning radiator |  |  |  |  | C0143 - Crank Shaft
2018-05-05 | XDRN003 (G#3) | 6917 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 99 | Cleaning condestator |  |  |  |  | C0144 - Cylinder Head
2018-05-08 | XDRN004 (G#4) | 7433 | Proactive Visit | C0095 - Radiator | A0013 - Preventative Maintenance | S0 100 | Cleaning radiator |  |  |  |  | C0145 - Exciter Stator/Rotor
2018-05-10 | XDRN003 (G#3) | 6992 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 101 | Cleaning flame trap |  |  |  |  | C0146 - Liners
2018-05-11 | XDRN001 (G#1) | 7485 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 102 | Cleaning flame trap |  |  |  |  | C0147 - PCB Assy - Analogue
2018-05-12 | XDRN004 (G#4) | 7477 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 103 | Cleaning flame trap |  |  |  |  | C0148 - Piston & Rings
2018-05-13 | XDRN002 (G#2) | 5956 | Proactive Visit | C0007 - Air Flap | A0013 - Preventative Maintenance | S0 104 | Cleaning flame trap |  |  |  |  | C0149 - Valve Springs
2018-05-14 | XDRN003 (G#3) | 7077 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | S0 105 | Cleaning condestator & Cleaning Air Filter |  |  |  |  | C0150 - Pipe Failure (Coolant, Oil, etc)
2018-05-15 | PLTMG RENGAT SOITEM | N/A | Proactive Visit | C0080 - Other "Written Description" | A0011 - Other "Written Description" | S0 106 | Site Compsumption Montly 1- Top Up on New oil Tank |  |  |  |  | C0151 - Battery Charger
2018-05-15 | XDRN002 (G#2) | 5969 | Reactive Visit, Breakdowns, Problems | C0075 - Motor Starter | A0018 - Replaced / Installed Component | S0 26 | Repair air stater Planetry gear |  |  |  |  | C0152 - Cam Followers
2018-06-11 | XDRN004 (G#4) | 7705 | Reactive Visit, Breakdowns, Problems | C0014 - Bearing - Failure | A0018 - Replaced / Installed Component | N/A | Replace throtle bearing 2 Pcs |  |  |  |  | C0153 - Connecting Rods
2018-06-18 | XDRN001 (G#1) | 7914 | Reactive Visit, Breakdowns, Problems | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap & Replaced throttle bearing |  |  |  |  | C0154 - Push Rods
2018-06-19 | XDRN004 (G#4) | 7824 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | N/A | Replaced spark plugs |  |  |  |  | C0155 - Mechanical
2018-06-19 | XDRN003 (G#3) | 7683 | Reactive Visit, Breakdowns, Problems | C0119 - Transducer | A0018 - Replaced / Installed Component | N/A | Replaced transmitter/transducer |  |  |  |  | C0156 - Power One DC Converter
2018-06-19 | SO ITEM | N/A | Proactive Visit | C0080 - Other "Written Description" | A0011 - Other "Written Description" | N/A | Site Compsumption Montly 1- Top Up on New oil Tank |  |  |  |  | C0157 - Spark Plugs
2018-07-02 | XDRN003 (G#3) | 7930 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap & throttle valve |  |  |  |  | C0159 - Audit
2018-07-20 | XDRN003 (G#3) | 8307 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | N/A | Replaced Air Filters |  |  |  |  | Site Consumption
2018-07-20 | XDRN004 (G#4) | 8325 | Proactive Visit | C0108 - Solenoid - Slave | A0017 - Repaired Component | N/A | Remove & cleaning wastegate
2018-07-21 | SO ITEM | N/A | Proactive Visit | C0080 - Other "Written Description" | A0011 - Other "Written Description" | N/A | Site Compsumption Montly 1- Top Up on New oil Tank
2018-07-25 | XDRN001 (G#1) | 8192 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | N/A | Replaced Air Filters
2018-07-31 | XDRN004 (G#4) | 8451 | Reactive Visit, Breakdowns, Problems | C0008 - Air Flow Blocked | A0039 - Repaired/Replaced by vendor | N/A | Replaced / installed CAC
2018-08-03 | XDRN004 (G#4) | 8451 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out B service (Valve lag check & adjustment)
2018-08-03 | XDRN002 (G#2) | 6226 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator
2018-08-03 | XDRN002 (G#2) | 6226 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Grasing Bearing Generator
2018-08-06 | XDRN001 (G#1) | 8302 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0017 - Repaired Component | N/A | Repair coolant manifold leaks cyl no. A7
2018-08-07 | XDRN003 (G#3) | 8617 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out B service (Valve lag check & adjustment)
2018-08-12 | XDRN004 (G#4) | 8561 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap & throttle valve
2018-08-14 | XDRN001 (G#1) | 8400 | Proactive Visit | C0157 - Spark Plugs | A0002 - Clean/Wash | N/A | Cleaning Spark Plug
2018-08-15 | XDRN002 (G#2) | 6485 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap & throttle valve & Spark Plug
2018-08-16 | XDRN002 (G#2) | 6506 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator
2018-08-17 | XDRN004 (G#4) | 8665 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator & Greasing generator
2018-08-17 | XDRN002 (G#2) | 8445 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-08-18 | XDRN002 (G#2) | 6535 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-08-20 | XDRN003 (G#3) | 8617 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-08-21 | XDRN004 (G#4) | 8747 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-08-22 | XDRN004 (G#4) | 8747 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2018-08-24 | XDRN003 (G#3) | 8617 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator
2018-08-28 | XDRN001 (G#1) | 8445 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator & Greasing generator
2018-08-29 | XDRN002 (G#2) | 6715 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning throttle valve
2018-08-30 | XDRN001 (G#1) | 8595 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap ( Vacum)
2018-08-31 | XDRN004 (G#4) | 8957 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator &Vacuum Flame trap
931981 | XDRN001 (G#1) | 8683 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter
2018-09-04 | XDRN002 (G#2) | 6804 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter /Flame Trap Cylinder A7 & A8 / Trottle Valve Side A / Condensator
2018-09-05 | XDRN004 (G#4) | 9048 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter
2018-09-05 | XDRN003 (G#3) | 8618 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter /Filter Generator
2018-09-05 | XDRN001 (G#1) | 8490 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment
2018-09-09 | XDRN003 (G#3) | 8620 | Reactive Visit, Breakdowns, Problems | C0075 - Motor Starter | A0018 - Replaced / Installed Component | N/A | Replacement Penumatic stater
2018-09-13 | XDRN004 (G#4) | 9092 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle bearing/spark plug/kondensator/Filter generator/air filter
2018-09-14 | XDRN004 (G#4) | 9092 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle bearing/spark plug/kondensator/Filter generator/air filter
2018-09-14 | XDRN001 (G#1) | 8923 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condestator
2018-09-17 | XDRN001 (G#1) | 8990 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle bearing/spark plug/kondensator/Filter generator/air filter
2018-09-24 | XDRN003 (G#3) | 8723 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle valve/spark plug
2018-09-26 | XDRN002 (G#2) | 7128 | Proactive Visit | C0102 - Sensor - Pressure | A0018 - Replaced / Installed Component | N/A | Replaced temp.sensor cyl.B3 & A7
2018-09-28 | XDRN004 (G#4) | 9148 | Reactive Visit, Breakdowns, Problems | C0065 - Magnetic Pick-Up | A0018 - Replaced / Installed Component | N/A | Replaced engine speed sensor (MPU)
2018-09-29 | SO ITEM | N/A | Proactive Visit | C0077 - No Problem Found | A0032 - Follow-up Required | N/A | site Consumption june 2018
2018-10-04 | XDRN002 (G#2) | 7286 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap, Spark plug & throttle valve
2018-10-05 | XDRN001 (G#1) | 9241 | Reactive Visit, Breakdowns, Problems | C0102 - Sensor - Pressure | A0018 - Replaced / Installed Component | N/A | Replaced thermocouple sensor cyl.B1 & B2
2018-10-06 | XDRN003 (G#3) | 8782 | Reactive Visit, Breakdowns, Problems | C0091 - Pump - Oil | A0001 - Adjusted Settings | N/A | Adjust engine oil pump due to low pressure
2018-10-06 | XDRN004 (G#4) | 9343 | Reactive Visit, Breakdowns, Problems | C0134 - Valve - Solenoid | A0017 - Repaired Component | N/A | Repaired wastegate malfunction
2018-10-07 | XDRN002 (G#2) | 7306 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning flame trap by vacuum
2018-10-08 | XDRN004 (G#4) | 9381 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Remove & Cleaning condensator
2018-10-13 | XDRN004 (G#4) | 9475 | Reactive Visit, Breakdowns, Problems | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replaced air Filters element
2018-10-13 | XDRN002 (G#2) | 7342 | Reactive Visit, Breakdowns, Problems | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replaced air Filters element
2018-10-15 | XDRN003 (G#3) | 8854 | Reactive Visit, Breakdowns, Problems | C0091 - Pump - Oil | A0017 - Repaired Component | N/A | Remove & cleaning oil pump spool regulator
2018-10-17 | XDRN001 (G#1) | 9470 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Remove & cleaning condensator
2018-10-18 | XDRN002 (G#2) | 7368 | Reactive Visit, Breakdowns, Problems | C0149 - Valve Springs | A0001 - Adjusted Settings | N/A | Adjust valve cyl.B6 due to low comb.temperature
2018-10-22 | XDRN001 (G#1) | 9540 | Proactive Visit | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | N/A | Replaced spark plug
2018-10-27 | XDRN004 (G#4) | 9738 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Remove&cleaning condesator
2018-10-29 | XDRN002 (G#2) | 7444 | Reactive Visit, Breakdowns, Problems | C0102 - Sensor - Pressure | A0018 - Replaced / Installed Component | N/A | Replaced thermocouple sensor cyl.B6
2018-11-01 | XDRN003 (G#3) | 9010 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle valve/spark plug
2018-11-01 | XDRN001 (G#1) | 9875 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Grasing Bearing Generator
2018-11-01 | XDRN004 (G#4) | 9720 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Grasing Bearing Generator/cleaning condesator
2018-11-03 | XDRN001 (G#1) | 9726 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2018-11-04 | XDRN003 (G#3) | 9038 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0019 - Replaced Filters | N/A | Carried out E40 Service @4000hrs, Oil result no. 790629 dated 6 nov 2017.
2018-11-06 | XDRN003 (G#3) | 9046 | Reactive Visit, Breakdowns, Problems | C0079 - Oil - Low/High | A0017 - Repaired Component | N/A | Reparied piston and cylinder regulatoroil
2018-11-08 | XDRN004 (G#4) | 9998 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Remove & cleaning condensator
2018-11-10 | SO ITEM |  | Reactive Visit, Breakdowns, Problems | C0080 - Other "Written Description" | A0011 - Other "Written Description" | N/A | modification piping line compressor #2
2018-11-12 | XDRN001 (G#1) | 9917 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | cleaning westgate
2018-11-06 | SO ITEM |  | Reactive Visit, Breakdowns, Problems | C0080 - Other "Written Description" | A0011 - Other "Written Description" | N/A | modification piping line compressor #2
2018-11-08 | XDRN003 (G#3) | 9165 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2018-11-10 | XDRN001 (G#1) | 10015 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle valve/spark plug
2018-11-19 | XDRN003 (G#3) | 9181 | Proactive Visit | C0117 - Thermostat | A0018 - Replaced / Installed Component | N/A | check motorize thrust actuator / thermostat 3 way
2018-11-22 | XDRN001 (G#1) | 10085 | Proactive Visit | C0155 - Mechanical | A0002 - Clean/Wash | N/A | Cleaning flame trap/throttle valve/spark plug
2018-11-23 | XDRN003 (G#3) | 9263 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Remove & cleaning condensator, Check / cleaning air starter
2018-11-23 | XDRN002 (G#2) | 7595 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter /Filter Generator/ cleaning condesator
2018-11-24 | XDRN003 (G#3) | 9269 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air filter generator
2018-11-26 | XDRN001 (G#1) | 10147 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter /Filter Generator
2018-11-27 | XDRN004 (G#4) | 10262 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter /Filter Generator/ cleaning condesator
2018-11-28 | XDRN004 (G#4) | 10285 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2018-11-29 | XDRN003 (G#3) | 9301 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning throttle valve & spark plug
2018-11-30 | XDRN002 (G#2) | 7633 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning spark plug & vacum flamtraff
2018-12-01 | XDRN001 (G#1) | 10235 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2018-12-03 | XDRN003 (G#3) | 9339 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-12-03 | XDRN002 (G#2) | 7646 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-12-04 | XDRN001 (G#1) | 10278 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-12-04 | XDRN004 (G#4) | 10407 | Proactive Visit | C0077 - No Problem Found | A0013 - Preventative Maintenance | N/A | Cleaning Radiator HT & LT
2018-12-08 | XDRN003 (G#3) | 9410 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2018-12-12 | XDRN004 (G#4) | 10507 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0017 - Repaired Component | N/A | Repair coolant manifold leaks cyl no.A7,A2 B6,B1
2018-12-15 | XDRN001 (G#1) | 10420 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0017 - Repaired Component | N/A | Repair coolant manifold leaks cyl no. B2 / Greasing Bearing Generator
2018-12-19 | XDRN004 (G#4) | 10564 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2018-12-22 | XDRN003 (G#3) | 9674 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2018-12-27 | XDRN002 (G#2) | 7723 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment
2018-12-31 | XDRN001 (G#1) | 10545 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out E40 Service @4000hrs, Oil result no. 790629
2018-12-31 | XDRN003 (G#3) | 9865 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning throttle valve & spark plug
2019-01-01 | XDRN004 (G#4) | 10803 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator
2019-01-02 | XDRN001 (G#1) | 10594 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning throttle valve & spark plug
2019-01-04 | XDRN001 (G#1) | 10613 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment
2019-01-07 | XDRN001 (G#1) | 10677 | Proactive Visit | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Install indicator Retriction
2019-01-07 | XDRN002 (G#2) | 7782 | Proactive Visit | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Install indicator Retriction
2019-01-07 | XDRN003 (G#3) | 9974 | Proactive Visit | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Install indicator Retriction
2019-01-07 | XDRN004 (G#4) | 10933 | Proactive Visit | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Install indicator Retriction
2019-01-11 | XDRN001 (G#1) | 10757 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-01-14 | XDRN004 (G#4) | 11094 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Remove & Cleaning condensator
2019-01-14 | XDRN003 (G#3) | 10059 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning throttle valve, spark plug, air folter & vacum flametrap
2019-01-15 | XDRN004 (G#4) | 11108 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning throttle valve, spark plug, air folter & vacum flametrap
2019-01-16 | XDRN004 (G#4) | 11114 | Reactive Visit, Breakdowns, Problems |  |  | N/A | Replace Seal coolant Manifold A8 & B7 ( leakage )
2019-01-17 | XDRN001 (G#1) | 10894 | Proactive Visit |  |  | N/A | Cleaning condensator & spark plug
2019-01-19 | XDRN003 (G#3) | 10126 | Proactive Visit | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Cleaning condensator , grease generator & replace Thermocouple cyl. B7
2019-01-21 | XDRN001 (G#1) | 10976 | Proactive Visit |  | A0013 - Preventative Maintenance | N/A | Cleaning Throttle valve
2019-01-21 | XDRN003 (G#3) | 10138 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | replace Thermocouple cyl. A5
2019-01-22 | XDRN004 (G#4) | 11195 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace Oring water manifold A7 and cleaning throttle valve
2019-01-23 | XDRN001 (G#1) | 11208 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0017 - Repaired Component | N/A | Repair leakage exhaust cylinder A8
2019-01-24 | XDRN003 (G#3) | 10207 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-01-25 | XDRN003 (G#3) | 10227 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap
2019-01-26 | XDRN002 (G#2) | 7945 | Proactive Visit | Site Consumption | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-01-27 | XDRN004 (G#4) | 11213 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out E40 Service @4000hrs
2019-01-30 | XDRN004 (G#4) | 11217 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component | N/A | Repair Flexible Hose Turbo B Side
2019-01-31 | XDRN004 (G#4) | 11230 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component | N/A | Repair Flexible Hose Turbo A Side
2019-01-31 | XDRN002 (G#2) | 8018 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter
2019-02-01 | XDRN001 (G#1) | 11197 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-02-01 | XDRN002 (G#2) | 8027 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-02-02 | XDRN001 (G#1) | 11216 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator, Air Filter dan Flametrap
2019-02-02 | XDRN002 (G#2) | 8046 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator
2019-02-03 | XDRN004 (G#4) | 11300 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-02-04 | XDRN002 (G#2) | 8046 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Trotle valve
2019-02-04 | XDRN004 (G#4) | 11320 | Proactive Visit | 50K - Oil Sample Due | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-02-04 | XDRN001 (G#1) | 11265 | Proactive Visit | 50K - Oil Sample Due | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-02-05 | XDRN003 (G#3) | 10380 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator,check oil stater,Cleaning ram generator
2019-02-07 | XDRN004 (G#4) | 11384 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator
2019-02-07 | SO ITEM |  | Proactive Visit | C0095 - Radiator | A0020 - Replenished Fluids (Coolant/Freon/Oil) | N/A | Added DCA to Coolant Tank
2019-02-08 | XDRN004 (G#4) | 11404 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning RAM Generator, check oil starter
2019-02-11 | XDRN003 (G#3) | 10474 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | replace Thermocouple cyl. A4
2019-02-11 | XDRN001 (G#1) | 11397 | Proactive Visit | 50K - Oil Sample Due | A0033 - Oil Sample Taken | N/A | Check Oil Starter
2019-02-12 | XDRN001 (G#1) | 11406 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning RAM Generator
2019-02-15 | XDRN001 (G#1) | 11432 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace Seal Manifold Cylinder A2,A3,A5,B1,B5 and B7 ; Repair Hose Flexible Turbo B Side
2019-02-16 | XDRN004 (G#4) | 11554 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace Seal Manifold Cylinder A2,B3,B4 and B7
2019-02-16 | XDRN001 (G#1) | 11442 | Reactive Visit, Breakdowns, Problems | C0109 - Starter - Engine | A0018 - Replaced / Installed Component | N/A | Repalce Check valve air stater
2019-02-18 | XDRN003 (G#3) | 10574 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve
2019-02-19 | XDRN003 (G#3) | 10578 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component | N/A | Repair Flexible Hose Exhaust Turbo Side A and B
2019-02-20 | XDRN001 (G#1) | 11477 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve and condensator
2019-02-23 | XDRN004 (G#4) | 11677 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator
2019-02-25 | XDRN003 (G#3) | 10642 | Reactive Visit, Breakdowns, Problems | C0157 - Spark Plugs | A0018 - Replaced / Installed Component | N/A | Replace Spark Plug & Cleaning Condensator
2019-02-25 | XDRN002 (G#2) | 8146 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check Oil Starter
2019-02-26 | XDRN004 (G#4) | 11731 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Cleaning throotle valve and replace seal manifold A3 & A4, Replace sealing ring 4 pcs
2019-03-03 | XDRN003 (G#3) | 10743 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace Thermocouple A1 and Replace Throotle Bearing A & B Side
2019-03-04 | XDRN003 (G#3) | 10765 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace Thermocouple B1
2019-03-06 | XDRN003 (G#3) | 10769 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check Oil Starter
2019-03-06 | XDRN004 (G#4) | 11821 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | N/A | Replace Air filter
2019-03-09 | XDRN003 (G#3) | 10776 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Adjust Valve Cylinder B1
2019-03-09 | XDRN002 (G#2) | 8180 | Reactive Visit, Breakdowns, Problems | C0043 - Fan | A0013 - Preventative Maintenance | N/A | Periodic Check of Fan Intake and Exhaust relevant to Unit #02
2019-03-12 | XDRN003 (G#3) | 10783 | Reactive Visit, Breakdowns, Problems | C0043 - Fan | A0013 - Preventative Maintenance | N/A | Periodic Check of Fan Intake and Exhaust relevant to Unit #03
2019-03-15 | XDRN002 (G#2) | 8229 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve
2019-03-16 | XDRN002 (G#2) | 8238 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out E40 Service @4000hrs
2019-03-18 | XDRN001 (G#1) | 11815 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator
2019-03-18 | XDRN003 (G#3) | 10894 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-03-18 | XDRN004 (G#4) | 12028 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-03-19 | XDRN004 (G#4) | 12048 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator, check oil air stater.
2019-03-21 | XDRN004 (G#4) | 12072 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Trotle valve
2019-03-22 | XDRN004 (G#4) | 12074 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace Seal Water Coolant Manifold A1, A2, A3, A4, A5 & Replace Gasket Exhaust Connection 2pcs
2019-03-23 | SO ITEM |  | Proactive Visit | C0095 - Radiator | A0002 - Clean/Wash | N/A | Radiator Cleaning Unit 1 , Unit 2, Unit 3, Unit 4 & Cleaning Main Pipe Line
2019-03-25 | XDRN003 (G#3) | 10964 | Proactive Visit | Site Consumption | A0002 - Clean/Wash | N/A | Cleaning Floor
2019-03-26 | XDRN002 (G#2) | 8297 | Reactive Visit, Breakdowns, Problems | C0073 - Motor Mech | A0017 - Repaired Component | N/A | Pre-heating pump motor Rewinding
2019-03-28 | XDRN003 (G#3) | 10977 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condesator
2019-03-29 | XDRN004 (G#4) | 12085 | Proactive Visit | C0043 - Fan | A0013 - Preventative Maintenance | N/A | Periodic Check of Fan Intake and Exhaust relevant to Unit #04
2019-03-31 | XDRN004 (G#4) | 12091 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Ram Generator
2019-04-01 | XDRN003 (G#3) | 10982 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Ram Generator
2019-04-02 | XDRN002 (G#2) | 8302 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Ram Generator
2019-04-05 | XDRN001 (G#1) | 11944 | Proactive Visit | C0043 - Fan | A0013 - Preventative Maintenance | N/A | Periodic Check of Fan Intake and Exhaust relevant to Unit #01
2019-04-08 | XDRN001 (G#1) | 11945 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace O Ring Water Manifold A6, A7, B7, B4
2019-04-09 | XDRN004 (G#4) | 12106 | Proactive Visit | Site Consumption | A0013 - Preventative Maintenance | N/A | Top Up Oil
2019-04-11 | XDRN002 (G#2) | 8313 | Proactive Visit | C0043 - Fan | A0013 - Preventative Maintenance | N/A | Periodic Check of Fan Radiator Unit #02
2019-04-16 | XDRN003 (G#3) | 11148 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Trotle valve & Flame Trap
2019-04-17 | XDRN001 (G#1) | 11153 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap
2019-04-18 | XDRN003 (G#3) | 11164 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning intake A8 & Spark Plug
2019-04-18 | XDRN004 (G#4) | 12140 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0018 - Replaced / Installed Component | N/A | Replace O Ring Fine Filter
2019-04-20 | XDRN002 (G#2) | 8314 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap
2019-04-20 | XDRN003 (G#3) | 11183 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Floor around unit
2019-04-21 | SO ITEM |  | Proactive Visit | C0095 - Radiator | A0013 - Preventative Maintenance | N/A | Site Consumption
2019-04-24 | XDRN001 (G#1) | 11989 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve
2019-04-24 | XDRN003 (G#3) | 11184 | Proactive Visit | C0059 - Hose / Fitting - Air | A0017 - Repaired Component | N/A | Repair Hose Flexible Turbo Side B
2019-05-01 | XDRN004 (G#4) | 12302 | Reactive Visit, Breakdowns, Problems | C0025 - Coolant Mixture / Level | A0018 - Replaced / Installed Component | N/A | Repaire water manifold ( connection piece )
2019-05-02 | XDRN004 (G#4) | 12302 | Proactive Visit | C0043 - Fan | A0013 - Preventative Maintenance | N/A | Periodic Check of Fan Intake and Exhaust relevant to Unit #04
2019-05-03 | XDRN004 (G#4) | 12302 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condesator
2019-05-04 | SO ITEM |  | Proactive Visit | C0150 - Pipe Failure (Coolant, Oil, etc) | A0013 - Preventative Maintenance | N/A | Site Consumption / Cleaning pipe in Gas Station
2019-05-10 | SO ITEM |  | Proactive Visit | Site Consumption | A0013 - Preventative Maintenance | N/A | site comsumtion ( Oil )
2019-05-11 | XDRN003 (G#3) | 12085 | Proactive Visit | C0008 - Air Flow Blocked | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap
2019-05-14 | XDRN002 (G#2) | 8338 | Proactive Visit | C0008 - Air Flow Blocked | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap ( Not comsumtion part )
2019-05-15 | XDRN001 (G#1) | 12114 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaninig trotle valve ( Not comsumtion part )
2019-05-16 | XDRN002 (G#2) | 8351 | Reactive Visit, Breakdowns, Problems | C0050 - Filter - Water | A0018 - Replaced / Installed Component | N/A | Repaire Connection piece B3
2019-05-19 | XDRN004 (G#4) | 12506 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment
2019-05-19 | XDRN003 (G#3) | 11308 | Proactive Visit | 50K - Oil Sample Due | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-05-21 | XDRN001 (G#1) | 12127 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator
2019-05-24 | XDRN004 (G#4) | 12534 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve
2019-05-26 | XDRN003 (G#3) | 11396 | Reactive Visit, Breakdowns, Problems | C0101 - Sensor - Level | A0018 - Replaced / Installed Component | N/A | Cleaning condensator,replace thermocople combustion camber
2019-06-01 | XDRN001 (G#1) | 12174 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning westgate,trotle valve
2019-06-01 | XDRN003 (G#3) | 12649 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning flametrape
2019-06-09 | XDRN004 (G#4) | 12807 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-06-11 | XDRN004 (G#4) | 12853 | Proactive Visit | 50K - Oil Sample Due | A0033 - Oil Sample Taken | N/A | Oil sample Taken
2019-06-12 | XDRN004 (G#4) | 12856 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condesator
2019-06-12 | XDRN003 (G#3) | 11489 | Proactive Visit | C0058 - Heater - Element/Electrode | A0017 - Repaired Component | N/A | Clear for look combution camber ( ok )
2019-06-18 | XDRN001 (G#1) | 12363 | Reactive Visit, Breakdowns, Problems | C0014 - Bearing - Failure | A0018 - Replaced / Installed Component | N/A | Replace bearing joint throttle valve shaft
2019-06-19 | XDRN002 (G#2) | 8453 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning throtle valve ( ok )
2019-06-21 | XDRN001 (G#1) | 12380 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condesator and RAM Generator
2019-06-23 | XDRN003 (G#3) | 11536 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check of Spark Plug A7, A8 and B2, B5
2019-06-25 | XDRN003 (G#3) | 11558 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning flametrape & RAM Generator, replace thermocouple A7,A8
2019-06-26 | XDRN001 (G#1) | 12410 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter
2019-06-27 | XDRN004 (G#4) | 13135 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator
2019-06-27 | XDRN002 (G#2) | 8463 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flametrape A7&A8
2019-06-28 | XDRN004 (G#4) | 13135 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator
2019-06-30 | XDRN001 (G#1) | 12446 | Proactive Visit | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component | N/A | Replace gasket Exhaust Manifold
2019-07-02 | SO ITEM |  | Proactive Visit | Site Consumption | A0013 - Preventative Maintenance | N/A | Top Up Oil
2019-07-02 | XDRN001 (G#1) | 12460 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning wastegate
2019-07-05 | XDRN001 (G#1) | 12479 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replace Air filter
2019-07-05 | XDRN002 (G#2) | 8520 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replace Air filter
2019-07-06 | XDRN003 (G#3) | 11762 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replace Air filter
2019-07-07 | XDRN002 (G#2) | 8533 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Condensator
2019-07-07 | XDRN003 (G#3) | 11779 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-07-07 | XDRN004 (G#4) | 13274 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replace Air filter
2019-07-08 | XDRN003 (G#3) | 11792 | Proactive Visit | C0150 - Pipe Failure (Coolant, Oil, etc) | A0017 - Repaired Component | N/A | Repaire Flexible Exhaust Manifold OK.
2019-07-08 | XDRN003 (G#3) | 11792 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator and check oil starter
2019-07-09 | XDRN002 (G#2) | 8537 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning RAM Generator
2019-07-13 | SO ITEM |  | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Maintenance of Gas Station
2019-07-15 | XDRN004 (G#4) | 13440 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Oil sample Taken & Cleaning Condensator
2019-07-17 | XDRN002 (G#2) | 8569 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Spark Plug / Busi
2019-07-18 | XDRN001 (G#1) | 12621 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator & Check Oil Starter
2019-07-18 | XDRN003 (G#3) | 11792 | Reactive Visit, Breakdowns, Problems | C0150 - Pipe Failure (Coolant, Oil, etc) | A0017 - Repaired Component | N/A | Install Flexible Exhaust Manifold
2019-07-19 | XDRN004 (G#4) | 13456 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve
2019-07-20 | XDRN001 (G#1) | 12639 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Air Filter
2019-07-21 | XDRN001 (G#1) | 12644 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap
2019-07-21 | XDRN002 (G#2) | 8607 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flametrap
2019-07-22 | XDRN001 (G#1) | 12655 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Throttle Valve
2019-07-23 | XDRN001 (G#1) | 12655 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment
2019-07-24 | XDRN001 (G#1) | 12667 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator and repair exhaust flexible B Side
2019-07-24 | XDRN003 (G#3) | 11931 | Proactive Visit | 50K - Oil Sample Due | A0033 - Oil Sample Taken | N/A | Oil Sample Taken
2019-07-25 | XDRN004 (G#4) | 13521 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment
2019-07-27 | XDRN004 (G#4) | 13548 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning RAM Generator
2019-07-28 | XDRN004 (G#4) | 13550 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing Bearing Generator
2019-08-02 | XDRN003 (G#3) | 12102 | Reactive Visit, Breakdowns, Problems | C0062 - Hose / Fitting - Water/Coolant | A0018 - Replaced / Installed Component | N/A | Replace Water manifold A1 & B3
2019-08-06 | XDRN004 (G#4) | 13716 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning condensator A&B
2019-08-07 | XDRN003 (G#3) | 12198 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning condensator A&B
2019-08-09 | XDRN003 (G#3) | 12227 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning trotle valve & Spark plug
2019-08-12 | XDRN001 (G#1) | 12931 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning condensator A&B
2019-08-20 | XDRN003 (G#3) | 12480 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning ram generator, condensator & check oil stater
2019-08-21 | XDRN004 (G#4) | 13997 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning Throttle Valve & ram generator
2019-08-24 | XDRN003 (G#3) | 12563 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing generator
2019-08-25 | XDRN004 (G#4) | 14043 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning condensator A&B
2019-08-29 | XDRN004 (G#4) | 14100 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning flametrap
2019-08-31 | XDRN001 (G#1) | 13229 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning trotle valve & Spark plug
2019-08-31 | XDRN004 (G#4) | 14133 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check and fill oil stater
2019-09-01 | XDRN003 (G#3) | 12727 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Valve lag check & adjustment, Cleaning spark plug,Trotle valve & Condensator
2019-09-03 | XDRN004 (G#4) | 14188 | Reactive Visit, Breakdowns, Problems | C0062 - Hose / Fitting - Water/Coolant | A0017 - Repaired Component | N/A | Repaire water manifold ( connection piece )
2019-09-03 | XDRN001 (G#1) | 13270 | Reactive Visit, Breakdowns, Problems | C0075 - Motor Starter | A0017 - Repaired Component | N/A | Repaire valve air stater
2019-09-04 | XDRN002 (G#2) | 8721 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing bearing generator
2019-09-04 | XDRN003 (G#3) | 12775 | Proactive Visit | C0008 - Air Flow Blocked | A0002 - Clean/Wash | N/A | Cleaning Air Filter
2019-09-04 | XDRN004 (G#4) | 14207 | Proactive Visit | C0008 - Air Flow Blocked | A0002 - Clean/Wash | N/A | Cleaning Air Filter
2019-09-06 | XDRN002 (G#2) | 8721 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning trotlevalve,repaire flexible exhaust,replace connection piece B8
2019-09-07 | XDRN004 (G#4) | 14272 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing bearing generator
2019-09-08 | XDRN001 (G#1) | 13345 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing bearing generator, Cleaning air filter
2019-08-21 | SO ITEM | All unit | Proactive Visit | Site Consumption | Site Consumption | N/A | site comsumtion ( Oil )
2019-09-09 | XDRN004 (G#4) | 14301 | Proactive Visit | C0087 - Preventive Maintenance Due | C0087 - Preventive Maintenance Due | N/A | Cleaning condensator A&B
2019-09-10 | XDRN004 (G#4) | 14301 | Reactive Visit, Breakdowns, Problems | C0062 - Hose / Fitting - Water/Coolant | A0018 - Replaced / Installed Component | N/A | Replace connection piece A8
2019-09-13 | XDRN001 (G#1) | 13410 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Repalce Air Filter
2019-09-13 | XDRN004 (G#4) | 14356 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Repalce Air Filter
2019-09-14 | XDRN003 (G#3) | 12794 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out E40 Service @4000hrs
2019-09-14 | All Unit |  | Proactive Visit | Site Consumption | Site Consumption | N/A | site comsumtion ( Oil )
2019-09-16 | XDRN003 (G#3) | 12986 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator and check oil starter
2019-09-17 | XDRN001 (G#1) | 13466 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator A&B
2019-09-17 | XDRN002 (G#2) | 8776 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator A&B
2019-09-17 | XDRN004 (G#4) | 14449 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | N/A | Replace air filter 4 pc ( Penggantian lebih cepat karena kabut asap dan debu )
2019-09-17 | XDRN003 (G#3) | 13012 | Proactive Visit | C0045 - Filter - Air | A0019 - Replaced Filters | N/A | Replace air filter 4 pc ( Penggantian lebih cepat karena kabut asap dan debu )
2019-09-19 | XDRN004 (G#4) | 14483 | Proactive Visit | C0159 - Audit | A0033 - Oil Sample Taken |  | Take oil sample
2019-09-21 | XDRN004 (G#4) | 14518 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning spark plug,trhotlle valve and flame trap
2019-09-22 | XDRN001 (G#1) | 13551 | Proactive Visit | C0159 - Audit | A0033 - Oil Sample Taken |  | Take oil sample
2019-09-22 | XDRN003 (G#3) | 13111 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Flame Trap
2019-09-23 | XDRN004 (G#4) | 14544 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator A&B
2019-09-27 | XDRN001 (G#1) | 13647 | Reactive Visit, Breakdowns, Problems | C0026 - Cooler - After | A0002 - Clean/Wash | N/A | Cleaning CAC A&B
2019-09-29 | XDRN003 (G#3) | 13233 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash | N/A | Cleaning Trotlevalve, Ram generator & Condensator A&B
2019-10-02 | XDRN004 (G#4) | 14671 | Reactive Visit, Breakdowns, Problems | C0061 - Hose / Fitting - Oil/Freon | A0018 - Replaced / Installed Component | N/A | Replace Hose Flexible,O ring plate cover
2019-10-03 | XDRN003 (G#3) | 13313 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing bearing generator
2019-10-03 | XDRN002 (G#2) | 8889 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check and fill oil stater
2019-10-04 | XDRN003 (G#3) | 13342 | Proactive Visit | C0159 - Audit | A0033 - Oil Sample Taken |  | Take oil sample
2019-10-05 | XDRN003 (G#3) | 13353 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning ram generator
2019-10-06 | All Unit |  | Proactive Visit | Site Consumption | Site Consumption | N/A | site comsumtion ( Oil )
2019-10-08 | XDRN003 (G#3) | 13406 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check and fill oil stater
2019-10-08 | XDRN004 (G#4) | 14787 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check and fill oil stater
2019-10-09 | XDRN001 (G#1) | 13706 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Check and fill oil stater
2019-10-12 | XDRN001 (G#1) | 13723 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning ram generator And condensator
2019-10-13 | XDRN004 (G#4) | 14904 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator A&B
2019-10-16 | XDRN003 (G#3) | 13580 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator A&B
2019-10-19 | XDRN001 (G#1) | 13816 | Reactive Visit, Breakdowns, Problems | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Replace Air Filter
2019-10-21 | XDRN004 (G#4) | 15041 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotlevalve, flametrape
2019-10-23 | XDRN003 (G#3) | 13671 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component | N/A | Replace Oring and connection piece A3&5,B2&8
2019-10-24 | XDRN004 (G#4) | 15111 | Proactive Visit | C0045 - Filter - Air | A0018 - Replaced / Installed Component | N/A | Change Air filter
2019-10-25 | XDRN003 (G#3) | 13702 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotlevalve, flametrape and change Air filter
2019-10-28 | XDRN004 (G#4) | 15175 | E40 - Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out E40 Service @4000hrs
2019-10-29 | XDRN001 (G#1) | 14000 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator A&B
2019-10-31 | XDRN002 (G#2) | 8959 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotlevalve
2019-11-01 | XDRN002 (G#2) | 8969 | Reactive Visit, Breakdowns, Problems | C0008 - Air Flow Blocked | A0019 - Replaced Filters | N/A | Replace Air Filter
2019-11-01 | XDRN004 (G#4) | 15193 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component | N/A | Replace gasket CAC and cleaning ( ok )
2019-11-09 | XDRN001 (G#1) | 14250 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing generator,cleaning condensator & Check oil stater
2019-11-11 | XDRN001 (G#1) | 14279 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotlevalve A& B
2019-11-14 | XDRN001 (G#1) | 14300 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning flametrape,spark plug
2019-11-15 | XDRN003 (G#3) | 14136 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Greasing generator,cleaning condensator & Check oil stater
2019-11-16 | XDRN003 (G#3) | 14136 | Proactive Visit | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component | N/A | Repaire Exhaust muffler
2019-11-20 | XDRN002 (G#2) | 9147 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotlevalve A& B, Spark plug
2019-11-22 | XDRN003 (G#3) | 14143 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning ram generator
2019-11-22 | All Unit |  | Proactive Visit | Site Consumption | Site Consumption | N/A | site comsumtion ( Oil )
2019-11-22 | XDRN001 (G#1) | 14401 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning ram generator
2019-11-26 | XDRN002 (G#2) | 9245 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning ram generator, Condensator
2019-11-27 | XDRN002 (G#2) | 9245 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotlevalve,take oil sample
2019-11-27 | XDRN004 (G#4) | 15557 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken |  | Take oil sample
2019-11-28 | XDRN003 (G#3) | 14258 | Reactive Visit - Non Failure | C0051 - Fluid Leaks | A0030 - Fabricated Component | N/A | Modified Blow by Filter
2019-11-29 | XDRN002 (G#2) | 9276 | Reactive Visit - Non Failure | C0051 - Fluid Leaks | A0030 - Fabricated Component | N/A | Modified Blow by Filter, Replace connection piece
2019-11-30 | XDRN004 (G#4) | 15608 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Carried out B service (Valve lag check & adjustment), Cleaning spark plug,Trotle valve & Condensator
2019-12-07 | XDRN001 (G#1) | 14443 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Westegate
2019-12-10 | XDRN001 (G#1) | 14449 | Reactive Visit, Breakdowns, Problems | C0101 - Sensor - Level | A0018 - Replaced / Installed Component | N/A | Replace thermocouple receive A
2019-12-10 | XDRN002 (G#2) | 9488 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator,fill oil stater,cleaning flametrap
2019-12-11 | XDRN004 (G#4) | 15782 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator, greasing generator,Air Filter
2019-12-12 | XDRN003 (G#3) | 14496 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning condensator,flametrap,air filter
2019-12-18 | XDRN003 (G#3) | 14573 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken |  | oil sample taken
2019-12-19 | XDRN004 (G#4) | 15890 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning ram generator
2019-12-21 | XDRN002 (G#2) | 9645 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning flametrap,trotlevalve,spark plug
2019-12-21 | XDRN004 (G#4) | 15998 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning Westgate
2019-12-22 | XDRN002 (G#2) | 9646 | Reactive Visit, Breakdowns, Problems | C0101 - Sensor - Level | A0018 - Replaced / Installed Component | N/A | Replace Thermocouple combustion chamber
2019-12-24 | XDRN003 (G#3) | 14697 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | N/A | Cleaning trotle valve,condensator,fill oil stater
2019-12-27 | XDRN002 (G#2) | 9695 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component | N/A | Replace connection piece A1-A7 & B6,B7
2019-12-27 | XDRN004 (G#4) | 16102 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken |  | oil sample taken
2019-12-30 | XDRN004 (G#4) | 16166 | Proactive Visit | C0059 - Hose / Fitting - Air | A0030 - Fabricated Component | N/A | Cleaning Trotlevalve and repaire flexible exhaust
2020-01-01 | XDRN003 (G#3) | 14868 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Valve lag check & adjustment
2020-01-02 | XDRN001 (G#1) | 14554 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | SERVICE @4000 Hours
2020-01-03 | XDRN003 (G#3) | 14903 | Proactive Visit | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Repaire flexible exhaust,cleaning condensator,Ram generatorfill oil air stater, greasing generator
2020-01-04 | XDRN002 (G#2) | 9799 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Valve lag check & adjustment, Cleaning condensator,take oil sample
2020-01-07 | SO ITEM |  | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Top oil to tangki storage ( 836 Ltr )
2020-01-11 | XDRN002 (G#2) | 9850 | Reactive Visit, Breakdowns, Problems | C0114 - Switch - Position | A0018 - Replaced / Installed Component |  | Inductive proximity sensor EA
2020-01-16 | XDRN001 (G#1) | 14650 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire Motor Fan Radiator HT 2 Pcs ( Test OK )
2020-01-18 | XDRN004 (G#4) | 16350 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repair Motor Pump Prelube Replacament Bearing
2020-01-20 | XDRN003 (G#3) | 15168 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0018 - Replaced / Installed Component |  | Repair Motor Pump Prelube Replacament Bearing
2020-01-21 | XDRN002 (G#2) | 10015 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator,Ram generatorfill oil air stater, greasing generator
2020-01-22 | XDRN001 (G#1) | 14932 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Valve lag check & adjustment , Cleaning condensator,air filter ,greasing,check oil stater
2020-01-26 | XDRN002 (G#2) | 10077 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Cleaning Trotle valve
2020-01-27 | XDRN002 (G#2) | 10077 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0030 - Fabricated Component |  | Repaire Flexible exhaust A&B
2020-01-29 | XDRN003 (G#3) | 15337 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Cleaning troltle valve,condensator,fill oil stater,replace thermocouple exhaust A
2020-01-29 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | Site comsumtion - Top up new oil
2020-01-30 | XDRN004 (G#4) | 16667 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken
2020-01-30 | XDRN004 (G#4) | 16667 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Cleaning condensator,greasing generator,check oil stater
2020-02-03 | XDRN004 (G#4) | 16710 | Reactive Visit, Breakdowns, Problems | C0157 - Spark Plugs | A0018 - Replaced / Installed Component |  | Replace New spark plugs All
2020-02-05 | XDRN001 (G#1) | 15130 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning flametrape,spark plug,condensator,ram generator
2020-02-05 | XDRN003 (G#3) | 15374 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0018 - Replaced / Installed Component |  | Replace bearing motor fan radiator
2020-02-06 | XDRN004 (G#4) | 16744 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component |  | Replace Seal water manifold
2020-02-06 | XDRN003 (G#3) | 15379 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | repaire motor fan radiator no.3&5 ( rewending motor )
2020-02-07 | XDRN003 (G#3) | 15379 | Reactive Visit, Breakdowns, Problems | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning CAC
2020-02-08 | XDRN002 (G#2) | 10301 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken
2020-02-16 | XDRN001 (G#1) | 15316 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken
2020-02-17 | XDRN001 (G#1) | 15330 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning flametrape
2020-02-17 | XDRN002 (G#2) | 10356 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning flametrape
2020-02-19 | XDRN004 (G#4) | 17008 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotle valve,condensator,ram generator and fill oil stater
2020-02-22 | XDRN001 (G#1) | 15402 | Reactive Visit, Breakdowns, Problems | C0014 - Bearing - Failure | A0018 - Replaced / Installed Component |  | Replace bearing motor water pump HT
2020-02-24 | SO ITEM |  | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Top oil to tangki storage ( 836 Ltr )
2020-02-26 | XDRN003 (G#3) | 15608 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken ( 2634 Hrs )
2020-02-26 | XDRN004 (G#4) | 17173 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken ( 1998 Hrs )
2020-03-04 | XDRN003 (G#3) | 15772 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire Motor Fan Radiator HT 1 Pcs ( Test OK )
2020-03-05 | XDRN002 (G#2) | 10588 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotle valve A&B
2020-03-06 | XDRN003 (G#3) | 15800 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotle valve A&B
2020-03-09 | XDRN001 (G#1) | 15711 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire Motor Fan Radiator HT 1 Pcs ( Test OK )
2020-03-12 | XDRN004 (G#4) | 17500 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotlevalve & Repaire flexible exhaust A
2020-03-16 | XDRN001 (G#1) | 15821 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken ( 1267 Hrs )
2020-03-16 | XDRN001 (G#1) | 15821 | Reactive Visit, Breakdowns, Problems | C0062 - Hose / Fitting - Water/Coolant | A0018 - Replaced / Installed Component |  | Replace O ring water manifold/connection piece
2020-03-17 | XDRN004 (G#4) | 17590 | Reactive Visit, Breakdowns, Problems | C0113 - Switch - Level | A0018 - Replaced / Installed Component |  | Replace thermocouple reciver B
2020-03-20 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | FILL DCA 4 FOR WATER RADIATOR
2020-03-21 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | Fill Oil site comsumtion ( 1254 ltr )
2020-03-23 | XDRN004 (G#4) | 17696 | E50 - MWM Periodic Maintenance (Extended) | C0087 - Preventive Maintenance Due | A0039 - Repaired/Replaced by vendor |  | Replace main bearing no.8( test load ok)
2020-03-24 | XDRN002 (G#2) | 10822 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken ( 2584Hrs )
2020-03-25 | XDRN001 (G#1) | 15856 | E50 - MWM Periodic Maintenance (Extended) | C0087 - Preventive Maintenance Due | A0039 - Repaired/Replaced by vendor |  | Replace main bearing no.8( test load ok)
2020-03-25 | XDRN003 (G#3) | 16103 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Oil Sample Taken ( 2584Hrs )
2020-03-26 | XDRN003 (G#3) | 16103 | E50 - MWM Periodic Maintenance (Extended) | C0087 - Preventive Maintenance Due | A0039 - Repaired/Replaced by vendor |  | Replace main bearing no.8
2020-03-30 | XDRN001 (G#1) | 15890 | Proactive Visit | C0025 - Coolant Mixture / Level | A0020 - Replenished Fluids (Coolant/Freon/Oil) |  | Change water coolant radiator HT & LT
2020-03-31 | XDRN003 (G#3) | 16202 | Proactive Visit | C0025 - Coolant Mixture / Level | A0020 - Replenished Fluids (Coolant/Freon/Oil) |  | Change water coolant radiator HT
2020-04-03 | XDRN001 (G#1) | 15976 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotlevalve
2020-04-06 | XDRN002 (G#2) | 10872 | Reactive Visit, Breakdowns, Problems | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning CAC A&B
2020-04-10 | XDRN003 (G#3) | 16296 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning Trotlevalve A&B
2020-04-15 | XDRN001 (G#1) | 16217 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning ram Generator,condensator,fill oil stater
2020-04-15 | XDRN003 (G#3) | 16313 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Repaire flexible exhaust A&B
2020-04-15 | XDRN003 (G#3) | 16313 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken | SO19628393002 | Oil Sample Taken ( 3339 Hrs )
2020-04-15 | SO ITEM |  | Proactive Visit | S1 - Site Consumption | S1 - Site Consumption |  | Site comsumtion Oil Myshella
2020-04-18 | XDRN002 (G#2) | 10959 | Proactive Visit | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning flametrape
2020-04-20 | XDRN002 (G#2) | 10973 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator,check and fill oil stater,greasing generator&motor wtp
2020-04-25 | XDRN001 (G#1) | 16347 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken | SO1964219400 | Oil Sample Taken ( 1793 Hrs )
2020-04-25 | XDRN003 (G#3) | 16473 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator
2020-04-30 | XDRN003 (G#3) | 16538 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire motor fan radiator HT (no.3 )
2020-04-30 | XDRN004 (G#4) | 18576 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire motor fan radiator HT ( no.10 )
2020-05-02 | XDRN003 (G#3) | 16550 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire motor fan radiator HT ( no.9&10)
2020-05-02 | XDRN004 (G#4) | 18563 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire motor fan radiator HT( no.4 )
2020-05-03 | XDRN001 (G#1) | 16500 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0039 - Repaired/Replaced by vendor |  | Repaire motor fan radiator HT( no.10)
2020-05-05 | XDRN003 (G#3) | 16585 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotle valve
2020-05-06 | XDRN001 (G#1) | 16558 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotle valve
2020-05-07 | XDRN001 (G#1) | 16558 | Proactive Visit | C0072 - Motor Failure - (Fan, Blower, etc.) | A0002 - Clean/Wash |  | On progres check motor water pump ( Test Ok )
2020-05-14 | XDRN002 (G#2) | 11098 | Reactive Visit, Breakdowns, Problems | C0024 - Controller - (HMI, PLC, I/O board, etc.) | A0017 - Repaired Component |  | Repaire actuator & actuator card ( Test run and load Ok )
2020-05-21 | XDRN002 (G#2) | 11115 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Repaire Flexible exhaust A&B
2020-05-23 | SO ITEM |  | Proactive Visit | S1 - Site Consumption | S1 - Site Consumption |  | Site comsumtion Oil Myshella
2020-05-25 | XDRN001 (G#1) | 16907 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0017 - Repaired Component |  | Repaire motor fan radiator No.2 & 11 HT
2020-05-25 | XDRN003 (G#3) | 16829 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator& fill Oil stater
2020-05-28 | XDRN002 (G#2) | 11177 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Greasing Generator
2020-05-30 | XDRN004 (G#4) | 19206 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | SERVICE @4000 Hours
2020-05-31 | XDRN004 (G#4) | 19216 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Greasing Generator, cleaning radiator
2020-05-31 | XDRN003 (G#3) | 16848 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Take Oil Sample( 3880 Hrs )
2020-06-13 | XDRN003 (G#3) | 16922 | Proactive Visit | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning trotle valve
2020-06-18 | SO ITEM |  | Proactive Visit | S1 - Site Consumption | S1 - Site Consumption |  | Site comsumtion Oil Myshella
2020-06-18 | XDRN002 (G#2) | 11373 | Reactive Visit, Breakdowns, Problems | C0157 - Spark Plugs | A0018 - Replaced / Installed Component |  | Replace spark plug 16 Pc & Cleaning trotlevalve
2020-06-19 | XDRN002 (G#2) | 11383 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Repaire flexible exhaust A&B
2020-06-22 | XDRN001 (G#1) | 17516 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Sample oil taken ( 2960 Hrs )
2020-06-22 | XDRN002 (G#2) | 11425 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Sample oil taken ( 3187 Hrs )
2020-06-22 | XDRN004 (G#4) | 19711 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Sample oil taken ( 500 Hrs )
2020-06-24 | XDRN001 (G#1) | 17555 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotlevalve,ram generator,condensator,greasing generator,fill oil air stater
2020-06-25 | XDRN003 (G#3) | 17037 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning ram Generator,condensator,fill oil stater,Greasing bearing generator
2020-06-28 | XDRN003 (G#3) | 17068 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | SERVICE @4000 Hours
2020-06-28 | XDRN004 (G#4) | 19845 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator & fill oil stater
2020-07-01 | XDRN003 (G#3) | 17074 | Reactive Visit, Breakdowns, Problems | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning CAC RB&LB
2020-07-10 | XDRN003 (G#3) | 17095 | Proactive Visit | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning flametrape
2020-07-11 | XDRN004 (G#4) | 20131 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning ram generator,greasing generator,cleaning condensator
2020-07-13 | SO ITEM |  | Proactive Visit | S1 - Site Consumption | S1 - Site Consumption |  | site comsumtion oil Myshella
2020-07-13 | SO ITEM |  | Proactive Visit | S1 - Site Consumption | S1 - Site Consumption |  | Site comsumtion DCA Coolant
2020-07-15 | XDRN001 (G#1) | 17911 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning flametrape & condensator
2020-07-16 | XDRN002 (G#2) | 11932 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning trotlevalve & Greasing generator
2020-07-17 | XDRN001 (G#1) | 17934 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning flametrape
2020-07-18 | XDRN004 (G#4) | 20286 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0017 - Repaired Component |  | Repaire motor fan radiator
2020-07-21 | XDRN004 (G#4) | 20350 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0017 - Repaired Component |  | Repaire motor fan radiator
2020-07-28 | XDRN002 (G#2) | 12202 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator dan filter udara
2020-07-29 | XDRN003 (G#3) | 17226 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Change filter udara bekas ( good condition )
2020-07-29 | XDRN001 (G#1) | 17999 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Change filter udara bekas ( good condition )
2020-08-03 | XDRN001 (G#1) | 18023 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken |  | Sample oil taken ( 3469 Hrs )
2020-08-04 | XDRN002 (G#2) | 12244 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0017 - Repaired Component |  | Replace Oring water manifold A8,B2
2020-08-05 | XDRN003 (G#3) | 17340 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator, fill oil stater
2020-08-06 | XDRN002 (G#2) | 12244 | Proactive Visit | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning trotlevalve A&B
2020-08-08 | XDRN002 (G#2) | 12261 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | SERVICE @4000 Hours
2020-08-11 | XDRN004 (G#4) | 20840 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator,ram generator, fill oil air stater, greasing generator,take sample oil ( 1634 )
2020-08-12 | XDRN003 (G#3) | 17436 | Reactive Visit, Breakdowns, Problems | C0008 - Air Flow Blocked | A0002 - Clean/Wash |  | Cleaning trotlevalve & Repaire flexible exhaust B
2020-08-18 | XDRN004 (G#4) | 20968 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning Trotlevalve dan chek flametrape ok
2020-08-24 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | Fill Oil site comsumtion ( 836 ltr )
2020-08-24 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | FILL DCA 65 FOR WATER RADIATOR
2020-08-25 | XDRN002 (G#2) | 12615 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator,flametrape,Fill oil stater,greasing generator,ram generator
2020-09-02 | XDRN002 (G#2) | 12794 | Proactive Visit | C0048 - Filter - Oil | A0033 - Oil Sample Taken | SO19872616 | Sample oil taken ( 533 Hrs )
2020-09-03 | XDRN002 (G#2) | 12798 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Replace flexible exhaust RB
2020-09-05 | XDRN003 (G#3) | 17595 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator
2020-09-09 | XDRN002 (G#2) | 12845 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Replace flexible exhaust LB
2020-09-16 | XDRN002 (G#2) | 12895 | Proactive Visit | C0087 - Preventive Maintenance Due | A0002 - Clean/Wash |  | Cleaning condensator
2020-09-19 | XDRN001 (G#1) | 18289 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Greasing bearing geneator
2020-09-19 | XDRN003 (G#3) | 17758 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Greasing bearing geneator
2020-09-19 | XDRN004 (G#4) | 21573 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Greasing bearing geneator
2020-09-21 | SO ITEM |  | Proactive Visit | S1 - Site Consumption | S1 - Site Consumption |  | Site comsumtion Oil Myshella
2020-09-22 | XDRN002 (G#2) | 12933 | Proactive Visit | C0065 - Magnetic Pick-Up | A0002 - Clean/Wash |  | Cleaning MPU speed engine
2020-10-30 | XDRN002 (G#2) | 12957 | Proactive Visit | C0121 - Turbo | A0002 - Clean/Wash |  | Check Turbo Glowing
2020-10-09 | XDRN003 (G#3) | 18011 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | S019873654 | Sample oil taken
2020-10-09 | XDRN004 (G#4) | 22041 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken |  | Sample oil taken
2020-10-14 | XDRN001 (G#1) | 18524 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | SO19880288 | Sample oil taken
2020-10-18 | XDRN001 (G#1) | 18607 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | SO19884397 | SERVICE @4000 Hours
2020-10-19 | XDRN003 (G#3) | 18238 | Proactive Visit | C0087 - Preventive Maintenance Due | A0001 - Adjusted Settings |  | Cleaning condensator,air filter and check oil stater
2020-10-20 | XDRN001 (G#1) | 18639 | Proactive Visit | C0087 - Preventive Maintenance Due | A0001 - Adjusted Settings |  | Cleaning condensator, Busi,change gasket cover valve
2020-10-21 | XDRN004 (G#4) | 22298 | Proactive Visit | C0087 - Preventive Maintenance Due | A0001 - Adjusted Settings |  | Cleaning ram generator,air filter,condensator,check oil stater,greasing generator
2020-10-23 | XDRN003 (G#3) | 18314 | Proactive Visit | C0087 - Preventive Maintenance Due | A0001 - Adjusted Settings |  | Cleaning trotlevalve
2020-10-24 | XDRN001 (G#1) | 18702 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0018 - Replaced / Installed Component |  | Replace motor fan radiator HT No.3,6,7,8,13,14
2020-10-27 | XDRN003 (G#3) | 18374 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0018 - Replaced / Installed Component |  | Replace motor fan radiator HT No.1,3,7
2020-10-28 | XDRN004 (G#4) | 22454 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0018 - Replaced / Installed Component | S019378030 | Replace motor fan radiator HT No.5
2020-10-30 | XDRN004 (G#4) | 22487 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S019949890 | Valve lag check & adjustment
2020-11-02 | XDRN004 (G#4) | 22552 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | S019905447 | Sample oil taken ( 3346 Hrs )
2020-11-03 | XDRN003 (G#3) | 18510 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | S019907206 | Sample oil taken ( 1442 Hrs )
2020-11-05 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | Site comsumtion Oil Myshella ( 627 ltr )
2020-11-10 | XDRN003 (G#3) | 18668 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Cleaning condensator,flametrape,air filer, greasing generator,fill oil stater
2020-11-12 | XDRN001 (G#1) | 19035 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S019949876 | Valve lag check & adjustment, Cleaning condensator,air flter,fill oil stater,greasing generator
2020-11-13 | XDRN001 (G#1) | 19043 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | S019923847 | Sample oil taken ( 436 Hrs )
2020-11-15 | XDRN004 (G#4) | 20350 | Reactive Visit, Breakdowns, Problems | C0072 - Motor Failure - (Fan, Blower, etc.) | A0018 - Replaced / Installed Component |  | Replace motor fan radiator HT No.7
2020-11-19 | XDRN003 (G#3) | 18861 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Cleaning trotlevalve
2020-11-20 | XDRN003 (G#3) | 18867 | E40 - MWM Periodic Maintenance (medium) | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance | S019949902 | Valve lag check & adjustment ( 4000 hrs )
2020-11-21 | XDRN003 (G#3) | 18894 | Reactive Visit, Breakdowns, Problems | C0101 - Sensor - Level | A0018 - Replaced / Installed Component |  | Replace thermocouple combustion chamber A1
2020-11-23 | XDRN004 (G#4) | 22882 | Reactive Visit, Breakdowns, Problems | C0055 - Gasket / ORing / Seal Failure | A0018 - Replaced / Installed Component |  | Replace Oring wtr manifold B6,cleaning ram generator,condensator,cek oil stater
2020-11-24 | XDRN001 (G#1) | 19174 | Proactive Visit | C0087 - Preventive Maintenance Due | A0013 - Preventative Maintenance |  | Cleaning trotlevalve
2020-11-25 | XDRN001 (G#1) | 19179 | Reactive Visit, Breakdowns, Problems | C0012 - Battery - Drained / Fault / Terminals | A0018 - Replaced / Installed Component |  | Replace batere panel
2020-11-28 | XDRN003 (G#3) | 19025 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | S019949921 | Taken oil sample ( 1957 hrs )
2020-11-30 | SO ITEM |  | Proactive Visit | Site Consumption | Site Consumption |  | Site comsumtion Oil Myshella ( 836 ltr )
2020-12-02 | XDRN003 (G#3) | 19085 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Replace flexible exhaust
2020-12-03 | XDRN004 (G#4) | 23096 | Proactive Visit | C0087 - Preventive Maintenance Due | A0033 - Oil Sample Taken | S019949963 | Oil sample taken
2020-12-03 | XDRN001 (G#1) | 19277 | Reactive Visit, Breakdowns, Problems | C0059 - Hose / Fitting - Air | A0017 - Repaired Component |  | Replace flexible exhaust