SIEMENS  Gas Turbine SGT  400

Scope of Supply & Additional Notes

Manufacturer	Siemens

Model	SGT-400

Year	2022

Condition	new

Category	Natural Gas Turbines

Subcategories	10 - 99 MW

Wattage	13 MW

Hours	Zero

Frequency	50/60 Hz

Fuel type	Natural Gas

Voltage	230 V

Un it s av ai lab le	3  x  13 M W U nit s, 50 / 60 H z

# SGT – 400 Gas Turbine Generator Set, with integral Local Equipment Room:

Units to be supplied are unused, with zero running hours, never installed.

Gas Turbine Package:

Original year of assembly: 2022 SGT 400 Gas Turbine Core Engine Original assembly location: Europe Never installed

AC  Generator:

Original assembly location: SIEMENS Electrical Machines Original year of assembly: 2022

Package and core engine serial numbers will be confirmed upon placement of order

The unit’s supporting documentation is available for review at any time with prior notice

Scope of Supply: Driven unit

AC Generator

230 V

- phases 50/60 Hz

- poles

0.8 power factor

Cylindrical pole brushless type Filter ventilated

Class F insulation with class F total temperature rise Generator bearing temperature instrumentation Lubricating oil piping from gas turbine to driven unit

Gas Turbine Engine

SGT 400 Gas turbine engine – ISO Rating 13 MW(e) – two-stage uncooled variable free power turbine offers nominal shaft speed up-to 6,600 rpm

Gas generator Air inlet casing

Compressor rotor

Compressor stator wit variable Guide Vanes (VGV) Centre casing

Combustion system – Dry Low Emissions (DLE) for dual fuels Compressor turbine rotor

Compressor turbine stator

Power turbine Hot gas interdict

Power Turbine rotor Power turbine stator Output shaft drive Exhaust outlet casing

Engine arranged for hot end drive

Engine bearing temperature and vibration instrumentation

Under base

Under base – fabricated carbon steel construction, arranged for - multi point mounting Mounting assemblies for the gas turbine core, auxiliary gearbox, auxiliaries, and main gearbox Driven unit – separate under base

Integral lubrication oil tank – carbon steel

Quantity 4 units SGT 400 generator packages available

Ready for shipment depending on site – specific requirements Gas and Liquid fuel system included

DLE combustion system

Start System

Hydraulic motor and pump – AC electric motor driven

Gears, Couplings and Guards

Gearbox seismic vibration instrumentation

Auxiliary gearbox incorporating drives to start system and lubricating oil pump Drive coupling – high speed – flexible element dry type – turbine to gearbox

Drive coupling – low speed – flexible element dry type – gearbox to AC generator Coupling guard – high speed – (carbon steel) – turbine to gearbox

Coupling guard – low speed – (carbon steel) – gearbox to driven unit

Lubricating Oil System

Integral mineral oil lubricating system serving the gas turbine, gearbox and driven unit Lubricating oil pump main – gas turbine gearbox driven

Lubricating oil pump auxiliary – AC motor driven Lubricating oil pump emergency – DC motor driven Lubricating oil system filter

Duplex filter arrangement

Continuous flow transfer valves Conforms to API 614

Filter body – carbon steel

Differential pressure indicator

Temperature and Smart type pressure & level transmitters – aluminium bodies Lubricating oil tank immersion heater

Lubricating oil system breather

Lubricating oil breather oil mist eliminator

Lubricating oil breather ducting – austenitic stainless steel Lubricating oil system cooler

Air blast simplex lubricating oil cooler – package roof mounted

Cooler fan – single (100% duty) Suitable for a non - hazardous area

Lubricating oil cooler piping supply and return – austenitic stainless steel

Gas Fuel System

Pilot fuel flow control system with actuator and integrated pressure transmitters Main fuel flow control system with actuator and integrated pressure transmitters Rapid acting gas shut – off – valves (2-off)

Temperature transmitter – aluminium body

Gas fuel block and vent valve assembly – off package

Acoustic Enclosure

Acoustic enclosure – painted carbon steel, fitted over gas turbine, gearbox and auxiliaries Doors for personal access and maintenance

83 dB(A)

Integral lifting beam for maintenance Integral lightning

Acoustic system transmitters – Siemens standard smart type – aluminium

Excluded – ground level enclosure access platforms and steps

Acoustic Enclosure Ventilation System Ventilation air inlet filter pad type

Enclosure ventilation inlet and outlet dampers – air operated

Ventilation fan – single – AC electric driven – Zone 2 Ventilation air system – negative pressure Ventilation air silencer

Ventilation air inlet and outlet ducting

Integral support for turbine enclosure ventilation system

Gas Detection System

Gas detection equipment comprising

- – I.R. point gas detectors (vent outlet)

Fire Protection System

Fire protection system comprising

- – I.R. multi spectrum flame detectors 2 – Heat detectors

Single sounder / beacon (end of package) 1 – Beacon (inside package)

Status indicator (end of package) 1 – MAC (Manual Alarm Contact)

Fire Extinguishing

Fire shot CO2 fire protection system – in accordance with NFPA 12 Cylinders housed in a weatherproof cabinet

Extinguisher system distribution pipework and nozzles Piping from cabinet to package

Combustion Air Inlet System

Combustion air filter – simple static element – painted carbon steel Combustion air filter – weather hood

Combustion air filter – mist eliminator Combustion air filter – EPA filter stage Combustion air silencer – painted carbon steel

Combustion air inlet ducting – painted carbon steel

Integral support for combustion air inlet system

Maintenance access platform and ladder – combustion air filter

Combustion Exhaust System

Exhaust diffuser – ferritic stainless steel – horizontal orientation

Exhaust silencer – ferritic stainless steel hot section – coated carbon steel outer casing Exhaust stack – ferritic stainless steel – floor standing vertical orientation – 15 m height Thermal insulation and aluminium cladding – personnel protection only

Package Electrical Systems

Integral Local Electrical Room (LER)

Designed to provide environmental protection for the SGT-400 package control panels and its operators. Fully equipped with lighting, power and environmental controls consisting of:

400 V AC – Package motors and heaters supply 230/110V 50/60Hz distribution board

Internal and external lighting Industrial 220/110V 50/60 Hz outlet

Air conditioning/heat pump unit capable of maintaining control room at 20°C in all ambient conditions A baseplate designed to support the control panel shelter and internal tread plates which will attach to the end of the SGT-400 package driver unit baseplate to allow for a single point lift of the driver package

A single control panel cubicle with support frame

The combined control panel will consist of a battery charger, unit control panel for turbine and generator control and monitoring and motor control centre

Batteries – VRLA type, sized to ensure a safe run-down of the turbine and driven unit in an emergency case

Package Auxiliaries

Turbine compressor – mobile cleaning system – 316 stainless steel tank – on and off-line wash Drain tanks on package

Auxiliary module pressure & level transmitters – Smart type – aluminium bodies Instrument tagging – row tags – SIEMENS standard P&ID references Package finish according to SIEMENS onshore standard

Control System

Package Control System Hardware

Control system mounted within integral LER

Unit Control System section – simplex, incorporating a SIEMENS SIMATIC PLC platform Control and monitoring of the package systems

Standard start-stop and load control functions – on-package control panel HMI PC panel mounted

Operator display language – English Machinery vibration monitoring

Ethernet TCP/IP communications data link to DCS Generator Control Panel section containing Automatic voltage regulator

Synchronizing facility – automatic & manual with check synchronizer Generator metering equipment and electrical protection

SIEMENS Turbomachinery Applications – Remote Monitoring System – STA-RMSTM STA-RMS allows improved support for engine operators

Required operation during warranty period and thereafter with Long Term Programs (LTP) service contracts

SIEMENS common Remote Service Platform secure communication through Virtual Private Network (VPN) via customer’s internet service STA-RMS primary functions:

Automatic transfer of engine operation data to Remote Diagnostic Centre allowing: Routine monitoring Predictive trending

Anomaly detection

Improved downtime prediction and scheduling Access to historic data

Fleet and unit performance reports

Remote access to the Human Machine interface allowing:

Direct operation of the Human Machine Interface by SIEMENS’ support personnel Software updates during fault rectification helpdesk call

Faster troubleshooting and support

Testing Gas Turbine

Gas turbine core engine test – SE standard – the core has already been tested. Test data available

Driven Unit Test

Manufacturer’s works acceptance test data of AC Generator. Pre-tested.

Installation and Maintenance Equipment

Roll-off equipment – Gas turbine power turbine Roll-off trolley – Gas Turbine core engine removal Maintenance equipment

Power turbine barring gear Core lifting equipment Semi-gantry crane

Auxiliary gearbox support

Installation tool kit comprising of a cabinet containing common hand tools Holding down fixings – GT and driven unit package

Holding down fixings – off-package equipment

Selection of paints for site repairs

Drawings and Documentation

Standard set of certified information an approval drawing in English language

Existing drawings are to be reviewed and issued with relevant modifications or a project specific cover Operator manual – English language – CD only

Maintenance manual – English language – CD only

Driven unit manual – English language – CD only Packing and Delivery

Packing

Packing and preservation to suit destination and transport method

Delivery terms

Delivered FCA Germany in accordance with ICC INCOTERMS 2020 edition

Spares

Commissioning equipment and tools Commissioning spares

Quality Assurance Contract QA Programme

Material Record Book (MRB) – quality assurance and as built records – English language

Subjects to prior sale – errors and omissions excepted

We quote as follows:

3 units SIEMENS Turbine SGT4 00

Price (3-units package):	EUR	37,600,000.00  /3 units

Delivery:	instant delivery, after full payment received,

10-15 days FCA Europe place according Incoterms*2020. Inspection possible

Payment:	10% escrow on order and prior to inspection

40% after inspection

50% before loading

All payments must be done on our given account issued in our commercial INVOICE.

Warranty:	12 months, after commissioning under

Siemens supervision.

ATTENTION!

Following exclusions are valid:

- Transportation, FCA truck loaded must be organized by purchaser.

- Foundation (concrete plateau), drawing by Siemens is part of documentation.

- Gas fuel connection to core turbine.

- Seller is not responsible for the ignitability (inappropriate gas) of the fuel gas provided.

This commercial offer is made in writing and represents the contract between Buyer and Seller with full knowledge of the facts above between both parties.

# Subjects to prior sale – errors and omissions excepted